DGS-30-326

(Rev. 07/21)

Special Requirements for Low Slope Roofing Membranes

Part 1 - General

  - Summary

- The provisions of this Section shall govern the installation of low-slope flexible membrane roofing in coordination with the roofing specifications.

- This section includes special provisions for low-slope roofing membranes on state-owned buildings.

- This section includes the coordination with the Owner’s roof consultant, inspection services provider, and full-time roof inspector.

  - Owner’s Roofing Inspection

- The Owner shall have a full-time roof inspector on site while the roof is being applied. The Contractor shall provide twenty-four (24) hours notice to the roof inspector prior to the installation of any roofing materials. The Contractor shall allow the roof inspector access to the work.

- Installation of roofing materials shall not be started without the roof inspector having a copy of the A/E approved Shop Drawings showing the ASTM’s or other standards of the roofing materials.

- The roof inspector will check all materials and application procedures and prepare a daily written report.

- A copy of the daily report shall be given to the General Contractor, A/E, and the Owner.

- The roof inspector’s scope of work:

- The inspector shall monitor the work for compliance with the Contract Documents

- The inspector shall continuously monitor and observe the work at the point of application during installation of the roof.

- The inspector shall immediately report any deficiencies or deviations to the architect and Owner. A written report shall follow an oral report within two business days.

- The inspector may recommend suspension of work or rejection of non-complying work to the A/E and Owner.

- The inspector shall not:

  - Authorize deviations from the Contract Documents.

  - Enter the area of responsibility of the Contractor.

  - Issue orders on any aspect of construction means, methods, techniques, sequences, procedures, or safety in connection with the work.

  - Pre-Roofing Conference

    - A pre-roofing conference is required and shall be held before ordering roofing materials.

    - Representatives of the Owner, roof inspector, Architect, General Contractor, roofing contractor, deck contractor, mechanical contractor, and roofing manufacturer shall attend.

    - Review of the plans, specifications, flashing details, work scheduling, and workmanship standards is required. Problems and discrepancies shall be resolved.

    - A written record of proceedings shall be prepared and made part of the job record.

  - Guarantees

- Provide the following roofing contractor’s guarantee on the General Contractor Guarantee form:

“The roofing contractor shall guarantee materials and workmanship associated with the roofing, flashings, and sheet metal work incidental to the work required under the roofing subcontract, against defect due to faulty materials or workmanship for a period of two (2) years from the Final Completion Date of the entire project. It is understood and agreed by all parties hereto that the responsibility of the roofing contractor under this guarantee form or any contract document, shall be in accordance with the roofing contractor’s limited guarantee.”

- Provide the following Owner’s Agreement on the General Contractor Guarantee form:

“The undersigned named Owner for the Commonwealth, agrees, from the Final Completion Date of the entire project, to maintain the roof in accordance with the manufacturer’s written requirements and also agrees to avoid damage to the roof surface by any parties under his control working or walking on the roof. The Owner recognizes his responsibility to inspect the roof semiannually.”

- Contractor’s Guarantee for New Construction (in no case shall the guarantee be less than as specified below, see membrane specification for additional warranty requirements, if any)

  - The (General) Contractor shall furnish, as a minimum, a manufacturer’s twenty (20) year total system material and labor warranty / guarantee with no monetary limitations (NDL no dollar limit) from the Final Completion Date of the entire project.

  - The Contractor shall provide a workmanship guarantee agreeing to maintain the entire roof system(s) in a completely watertight condition at no cost to the Owner for two (2) years from Final Completion Date of the entire project. Sheet metal flashing incidental to the roofing shall be covered under the manufacturer’s warranty.

- Contractor’s Guarantee for Reroofing (in no case shall the guarantee be less than as specified below, see membrane specification for additional warranty requirements, if any)

  - The (General) Contractor shall furnish, as a minimum, a manufacturer’s twenty (20) year total system material and labor warranty / guarantee with no monetary limitations (NDL no dollar limit) from the Final Completion Date of the entire project.

Exception: Roofs measuring less than 5,000 square feet in area and roofs on utility or unoccupied structures shall have a minimum ten (10) year total system warranty.

  - The Contractor shall provide a workmanship guarantee agreeing to maintain the entire roof system(s) in a completely watertight condition at no cost to the Owner for two (2) years from Final Completion Date of the entire project. Sheet metal flashing incidental to the roofing shall be covered under the manufacturer’s warranty.

  - Materials Certification

- The materials shall be labeled with ASTM certification numbers or other specified product certifications or the Contractor shall give to the A/E the roofing manufacturer’s certification that the roofing materials being furnished comply with specified ASTM and approved standards.

- The Owner’s full-time roof inspector shall verify the materials received are as specified and in accordance with A/E approved shop drawings before roofing materials may be installed.

  - Roofing Manufacturer’s Inspections

- The roofing manufacturer’s representative shall inspect the roofing installation procedures at the start of the roofing membrane installation and inspect the completed installation

  - Wind Uplift and Edge Securement

- Low slope membrane roofs, except gutters, shall be designed and installed for wind resistance in accordance with ANSI/SPRI ES-1.

  - Approved Applicator

A.	The roofing and base flashing applicator shall be approved by the materials

manufacturer.

  - Roof Protection

- Before moving equipment or materials over a roof, the Owner, general Contractor, roofing Contractor, and any of their agents must protect the roof from damage during and following roofing work.

- Movement of equipment and materials without roof protection shall be cause for the Owner, general Contractor, roofing Contractor to stop work until protection is provided and any damage is corrected.

- The Owner's roofing inspector shall record all such violations.

  - Pre-Final Inspection Survey

Unless the Owner requests, in writing, a waiver of the survey for justifiable reasons and has been approved by the Director of DEB, comply with the following provisions:

- The A/E shall notify, in writing, the Owner, Contractor, and roofing Contractor that he has inspected the roof(s) and finds it (them) sufficiently complete to permit a roofing survey. In no case shall the survey be made earlier than forty (40) days before the Substantial Completion inspection.

- The Owner shall engage the services of an experienced and independent roof survey inspection service or laboratory to survey the roof(s). The service shall use infrared, nuclear moisture detection, impedance survey or electronic leak detection methods. Roof probes or cuts shall not void the Contractor’s two (2) year workmanship warrantee and the manufacturer’s warranty/guarantee.

- The roofing Contractor shall cooperate and assist the inspection service by making and repairing any required cores, test cuts, or probes in such a way that Manufacturer's and Contractor's warranty/guarantees are not voided.

- Copies of all survey reports shall be delivered to the Owner, DEB, A/E, general Contractor, and roofing Contractor no later than ten (10) days before the Substantial Completion inspection.

- The Owner shall pay for the service unless the survey shows roofing deficiencies caused by improper materials, poor workmanship, or Contractor negligence. In that case the Contractor, at his expense, shall repair or replace the roof(s) and provide additional surveys until the roofing work complies with the Contract Documents. All corrective work shall be completed before the final inspection.

- Acceptance of the roofing system shall be contingent on a roofing survey report that indicates the presence of no detrimental amount of moisture; for example, moisture that would cause a significant lowering of the thermal resistance of the roof; separation of the roofing plies; blisters; etc. Insulation or roofing materials determined in the roof survey to have detrimental amounts of moisture by the inspection service provider and any materials covering the insulation shall be replaced by the Contractor at no cost to the Owner.

- In any case where the roofing survey reports insulation that has lost more than 20% of its dry thermal resistance (R-value) the (wet) insulation and any materials covering the insulation shall be replaced by the Contractor at no cost to the Owner.

  - Final Inspection

The following items must be given to the Owner's representative at the Final Inspection:

- A copy of the (general) Contractor’s and roofing Contractor’s two-year guarantee.

- A copy of the roofing manufacturer’s standard warranty/guarantee.

  - One (1) Year  Inspection

Representatives of the Owner (and the A/E), the Contractor, the roofing subcontractor, and the membrane manufacturer shall inspect the roof(s) between nine (9) months and one (1)  year before the closing of the General Contractor’s one (1) year guarantee.

  - Two (2) Year Inspection

The Owner shall also have the roof inspected at least three (3) months before the two (2) year guarantee expires and notify the Contractor in writing of any defects noted. The Owner shall require that any defects be corrected at least thirty (30) days prior to expiration of the guarantee.

Part 2 Products (Not Used) See Roof Membrane Specifications

Part 3 Execution

3.1	Roof Slope

A	All roofs shall slope 1/4" per foot, minimum, to drains on all new roofs, unless otherwise specified.

B.	Dead level valleys are unacceptable. Cricket valleys shall slope a minimum of 1/8" per foot unless otherwise specified.

3.2	Insulation

Unless otherwise required to comply with a manufacturer’s roofing system, or by DEB approved waiver, insulation installation shall be as follows:

A.	Meet C or R (per inch factor) value as specified elsewhere.

B.	Provide a minimum of two (2) layers, if thickness permits

C.	Provide staggered joints between layers of the insulation.

D.	Fasten the insulation as required elsewhere in the specifications. If no requirements are listed mechanically fasten the first layer to metal deck. Cold applied adhesives and/or low rise foam products are acceptable for the attachment of the first layer to concrete decks, and for attachment of the individual insulation layers to each other contingent upon meeting FM I-90 wind uplift rating and the specified roofing material manufacturer’s warranty.

E.	Compatible Insulation: The A/E shall ensure the type of insulation specified is entirely compatible with contiguous, specified roofing materials.

3.3  	Rooftop Equipment

A.	Provide design clearances and details for easy re-roofing.

B.	Comply with NRCA Manual recommendations for minimum height of equipment above the roof membrane when equipment is supported above the roof surface.

C.	Provide prefabricated walks to and around equipment that requires servicing. Walks must not block roof drainage.

3.4	Vegetative Roofs, if specified elsewhere, shall meet the following minimum requirements:

Vegetative roof shall be installed per requirements in FM Data Sheet 1-35 criteria except as indicated in the building code. Wind load design criteria shall be in accordance with ASCE 7 instead of 1-35 criteria.

A.	Non-vegetated border zones

1.	Shall be per FM 1-35 requirements at perimeters and corners

2.	Shall be a minimum eighteen (18) inches wide at penetrations

3.	Shall be a minimum three (3) feet wide at machine rooms, penthouses, and walls

4.	Shall be a minimum three (3) feet wide to partition the roof area, not exceeding 15,625 square feet and one-hundred twenty-five (125) feet in length. See the building code for additional requirements.

B.	Parapet walls

    - Shall be a minimum of six (6) inches above ballast or pavers for roofs below one-hundred fifty (150) feet in height.

    - Shall be a minimum of thirty (30) inches in height for roofs one-hundred  fifty (150) feet or above in height and shall have a three (3) foot wide non-vegetative zone.

C.	Grade level roofs

1.	Shall have special load requirements

2.	Shall have a three (3) foot vegetation free break.